## Slide 1: PowerPoint 6: Drainage components
PowerPoint presentation
Unit 112: Construction operations and civil engineering operations

## Slide 2: Types of pipes and joints
Rigid, if made of cast iron, concrete, asbestos cement,
Flexible, if made of plastic materials, pitch fibre, clay or similar materials; and steel, etc.
Joints are considered:
Rigid, if made solid by using sand/cement joints or by welding or bolting the flanges of metal pipes
Flexible, if joints are made with deformable rings or gaskets held between pipe spigots and sockets, sleeves or collars.

## Slide 3: Vitrified clay – pipes
Made from:
Clay with salt glaze added during firing in a kiln
Used for:
Domestic and industrial drains and sewers
UPVC – pipes
Made from:
Un-plasticised polyvinyl chloride
Used for:
Domestic drains and sewers

## Slide 4: Concrete – pipes
Made from:
Good quality, small aggregate concrete
Used for:
Water supplies and industrial waste drains
Pitch fibre – pipes
Made from:
Pitch with fibres added and moulded into various pipe sizes
Used for:
Field drainage and ducts for telephone wires, electrical cables and other cables passing through walls into a building

## Slide 5: Conduits
These are used mainly as ducting to carry electrical or telephone wiring, particularly when wires have to pass through a building or be buried in plaster walls.
Jointing compound
This can be used to connect UPVC pipes and couplers together. It is also used when connecting rain water pipes and couplers: the jointing compound is painted onto both pipe and coupler and the connection made immediately. The compound melts the material and, on drying, forms a watertight joint.

## Slide 6: Couplings and connectors
These are used to connect both UPVC and pitch fibres to each other. These are known as flexible joints whereas vitrified clay pipes and concrete pipes usually have a spigot at one end and a collar at the other.
These types of pipes normally have sand/cement joints which are known as rigid joints.

## Slide 7: Commonly used joints
Double spigot – provides a butt joint with a polypropylene coupling sleeve which encloses the ends of the pipe
Spigot and socket – joint sealed with the use of a rubber ring placed between the male (spigot) and female (socket) ends of the pipe

## Slide 8: Spigot and socket, salt glazed clay pipes
For many years this was the standard type of drainage pipe and required a cement hand mortared joint. This was made after caulking the joint with a length of tarred yarn wrapped round the spigot and caulked into the socket. This type of pipe and joint is suitable for foul water drainage systems.

## Slide 9: Spigot and socket, vitrified clay pipes
These pipes are self-aligning, flexibly joined and self-sealing. They are a modern alternative to the traditional spigot and socket glazed ware and are easier and quicker to lay. They are suitable for foul drainage and are available in 150, 225, 300, 375 and 450mm diameters.

## Slide 10: Double spigot vitrified clay pipes with flexible couplings (hepsleve or similar)
This provides a butt joint with a polypropylene coupling sleeve which encloses the pipe ends as shown. It is acceptable for either storm or foul water drainage and is available in 100 and 150mm diameters.

## Slide 11: UPVC (unplasticised polyvinyl chloride)
These pipes are flexible, are usually up to 6 m long in 110, 160 and 200mm diameters and are very light to handle.
The pipes have either a tight push fit into the coupling joint or have a push fit into a flexible coupling joint.
Care must be taken when pushing a pipe into the joint sleeve to use a tool which will not mark the face of the pipes (e.g. crowbars are not suitable).

## Slide 12: Drainage fittings
There are different types of drainage fittings and components available from a variety of manufacturers, these include sockets, bends, rest bends and junctions. All of these are available in a number of sizes and angle/degree of bend.

## Slide 13: Couplings and adaptors
Standard coupling
Drain coupling
Drainage adaptor
Universal adaptor

## Slide 14: Standard coupling
Standard couplings are primarily used in sewer, drain and other non-pressure applications.
Public sewers.
As an alternative to a traditional coupling for plain ended pipes.
Where a post connection is required into an existing drain or sewer.
For insertion of a new pipe in order to replace a damaged section of existing sewer or drain.
Where the pipe to be replaced is a different diameter and material to that of the replacement pipe.
Where pipes have been cut or short lengths of pipe require jointing.

## Slide 15: Drain coupling
Uses:
As an alternative to a traditional coupling for plain ended pipes.
For insertion of new pipe in order to replace a damaged section of existing sewer or drain.
Where the pipe to be replaced is a different diameter and material to that of the replacement pipe.
Where pipes have been cut or short lengths of pipe require jointing.
For use in vertical drainage applications where the pipes jointed are not subject to any loading.
www.youtube.com/watch?v=94aKj8eJDfo&feature=player_embedded

## Slide 16: Gullies
Gullies can be used to remove surface water from paved pedestrian areas. Side and back boss inlets accept waste water from ground floor domestic appliances and/or rainwater from roofs.

## Slide 17: Pre-cast or pre-formed manholes
Manholes were built entirely in brickwork many years ago. It is now more convenient to use pre-cast concrete or pre-formed plastic manholes which are available in sections varying in depths from 100mm to 600mm.
The bottom section of these have the necessary channels and junctions, so making the formation of a manhole much quicker and easier, particularly in waterlogged ground.

## Slide 18: Manholes
All sewer pipelines must be laid in straight lengths to a constant gradient over each length.
A manhole is required at every change of:
(a) direction
(b) gradient
(c) pipe size
(d) pipe type

## Slide 19: Manholes
Where several lengths of sewer join together, a manhole or inspection chamber should be built.
For long straight lengths of sewer, manhole or inspection chambers are often provided at not more than 100m intervals.
Manholes are provided so that the sewer can be rodded in case it gets blocked.

## Slide 20: Manholes
The manhole should have a strong cover and frame.
The access shaft should be at least 550mm wide and preferably 600mm wide.
Step irons should be provided every 300mm when needed.
There should be adequate headroom for workers to work safely in the manhole.
The benching must have a crossfall, but should not be too steep for workers to stand on it.
The manhole should be watertight.

## Slide 21: Manhole construction
There are three main methods/materials used in the construction of manholes.
Brick walls on concrete base and with concrete cover slab built in situ, rectangular in shape.
Precast concrete rings which build up into a circular section manhole and which are set on a concrete base.
Plastic prefabricated manholes, also circular in section, with each ring flanged and bolted together.

## Slide 22: Inspection chamber
These are normally shallow, rectangular or circular in shape, with a cover and frame which are the size of the chamber. Workers operate from above ground when rodding a drain from an inspection chamber.

## Slide 23: Rodding eye
This is provided at the uphill end of a sewer where the depth is not great and where there is no need to provide a manhole, which would be much more expensive.

## Slide 24
Any questions?