## Slide 1: PowerPoint 7: Drainage laying and testing
PowerPoint presentation
Unit 112: Construction operations and civil engineering operations

## Slide 2: Pipe sizes and gradients of pipelines
A minimum 100mm diameter pipe is usually adequate for most domestic drain pipelines.
Up to 20 houses can be connected to a 100mm diameter drain because only one or two houses are likely to discharge waste water at the same time.
In some housing developments, 150mm diameter drains may be used.

## Slide 3: Gradients
The gradient determines the speed of discharge and it is important to ensure that adequate flow occurs in order that the drain remains self-cleansing. The fall of the drain should, where possible, follow the natural contours of the ground in order to reduce excavation work.
Recommended gradients are as follows:
Diameter (mm) Gradient
100 1:40
150 1:60
225 1:90

## Slide 4: Trench formation
To ensure uniform support along the pipeline, it is essential to remove all hard or soft spots which may cause differential settlement and replace them with tamped, selected backfill.
The important points to remember when forming and stabilising trenches are:
the nature of the ground
the depth of the trench
the depth of water table and permeability of the soil.

## Slide 5: Bedding for pipes
Flexible pipes should be laid in a granular material which must be firmly and evenly compacted to support the pipeline all around.
Laying flexible pipes directly on the trench bottom is not recommended because of the difficulty in getting a uniform support for the pipeline.
Ideally, granular material sized 5 to 10mm should be used as it requires very little tamping.

## Slide 6: Granular bedding
The most suitable material for granular bedding is ‘nominal single size material’ to BS 882, the maximum size being related to the pipe diameter as follows:
100mm diameter pipes - 10mm nominal size aggregate
150mm diameter pipes - 10 to 14mm nominal size
225mm diameter pipes - 10, 14 or 20mm nominal size

## Slide 7: Placing the bedding material
(a) Check from established levels that the correct thickness of bedding can be laid. If not, the trench bottom must be trimmed.
(b) Place bedding material in trench and spread to correct level.
Pipe selection and handling
Check that the correct size and type of pipe is available and inspect for defects, i.e. chips, cracks, damage to joints, etc. Reject where necessary.
(b) Place pipes ready for laying alongside the trench at 45⁰ to the edge.
(c) Lower larger pipes onto bedding material using a sling.

## Slide 8: Laying
Clean pipe ends.
(b) Lay the pipe to line and level working uphill. If spigot and socket pipes are being used, they should be laid with the socket uphill. When laying pipes, cut holes to accommodate the socket or joint into the trench bottom or bedding, so that the pipes will lie with the length of the pipe barrel supported by the ground.
(c) Check that the highest point of the pipe is 1–3 mm below the line for the centre line method, or that the laser beam is correct for line and level.
(d) Lay subsequent pipes and form joints.
(e) Check the complete pipe line for line and level and, if used, remove line and pins.

## Slide 9: Backfilling
(a) Supervisor to give permission prior to backfilling.
(b) This backfill should be carefully compacted, to avoid disturbance of the pipes, and to a depth of 300mm above the barrel of the pipes.
(c) Thereafter, backfill should continue, layers of about 150mm being compacted successively until the backfill is completed.
(d) If turf was removed prior to excavating then re-lay on a bed of about 100mm of topsoil which is only lightly compacted.
(The construction of manholes has been left out at this stage but would normally proceed at the same time as the drain laying.) All surplus materials and equipment are then removed and the site left clean and tidy.

## Slide 10: Inspection and testing
Site inspections and tests are necessary to ensure that materials and components are properly installed so that they will operate effectively and that the drainage system will not cause a risk to health.

## Slide 11: First stage inspection and testing
Tests may include visual inspection for line and level, joints, damage or deformation, connections, linings and coatings.
The standard specifies that the vertical change in diameter of flexible pipes shall be checked for compliance with the design. Inspection of the pipeline will also reveal any defects in the support and bedding.
Testing for leak tightness includes the testing of connections, manholes and inspection chambers.

## Slide 12: Final testing
Testing and inspection should take place immediately before handover when all relevant works have been completed.
A water test is generally preferred since it relates very closely to the conditions found in practice.
It does, however, suffer from the disadvantage of providing and disposing of large quantities of water.

## Slide 13: Final testing
An air test is easier to apply but the results can be affected by small changes in temperature. A change in temperature of 1⁰C will result in a corresponding change in air pressure of about 38mm water gauge. Therefore, if the pressure drop is above that recommended, the pipeline should not be deemed unsatisfactory on the air test alone.
The number of air tests allowed to be carried out is not restricted but where recourse is made to the water test, it shall alone be decisive.

## Slide 14: Water test
Drains should be tested to a pressure of 1.5m head above the invert of the pipe at the high end of the pipe and not more than 4m head at the lower end. Testing should be carried out between manholes, inspection chambers or any other suitable access points and carried out using the following steps:
Fit stoppers at the lower end of the pipeline to seal off a section for testing.
Also fit a stopper at the top end of the pipeline together with a standpipe or flexible tube leading from a container connected to the plug.
Continued…..

## Slide 15: Water test (continued)
(c) Fill the pipeline with water, making sure there are no pockets of trapped air.
(d) Fill the standpipe to a height of 1.5m above the pipe invert.
(e) Allow the pipeline to stand for 2 hours for absorption, topping up as required.
(f) After 2 hours measure the loss of water by noting the quantity of water needed to maintain the test head in the apparatus over a 30-minute period.
The rate of water loss should not exceed 1 litre/hour per metre run. This is equivalent to 0.05 litres per metre run for a 100mm pipe if the test is satisfactory.

## Slide 16: Air test
The test is carried out by inserting plugs or inflatable bags in the upper and lower ends of the pipeline and pumping in air under pressure. A glass U tube gauge (manometer) and the air pressure source are connected.
Air pressure is then applied by mouth or hand pump to achieve the required test pressure.

## Slide 17: Air test
Testing should be carried out between manholes, inspection chambers or other suitable access points using the following steps:
Fit plugs into the ends of the pipeline and all associated branches.
(b) Connect a manometer to one of the plugs and a means of supplying air to another plug.
(c) Apply pressure by mouth or hand pump to achieve a pressure of slightly more than 100mm water gauge for pipelines or 50mm where ground floor appliances or gullies are connected.
(d) Allow 5 minutes for stabilisation of air temperature.
(e) Adjust air pressure to 100mm or 50mm as appropriate.

## Slide 18: Air test
The test is deemed to be acceptable if, without further pumping, the head of water does not fall by more than 25mm in a period of 5 min for a 100mm water gauge or by more than 12mm for a 50mm water gauge.

## Slide 19
Any questions?