## Slide 1: PowerPoint 4: Drainage systems
PowerPoint presentation
Unit 112: Construction operations and civil engineering operations

## Slide 2: Introduction
The purpose of a below ground drainage system is to convey waste water from sanitary fittings, such as sinks, baths, etc. and also surface water from roofs, driveways, paths, etc. to larger communal pipes known as sewers.
The priorities for a good drainage system are as follows:
The design should be simple and economic.
Drains must be laid at suitable gradients.
The flow of waste water (effluent) should be self-cleansing.
The effluent should be conveyed without leakage.
All relevant regulations and standards must be complied with.

## Slide 3: Combined system
In some drainage systems, particularly older systems, both waste water and surface water are discharged into a common drain or sewer. This system is known as a combined system, as all building drainage is combined into one drain or sewer.
The problem with this type of system is that surface water which is relatively ‘clean’ is mixed with waste water and, therefore, must undergo the same treatment process as waste water.
Treating surface water to this extent is neither necessary or economical. It may also present a health risk during storm conditions if the sewer is unable to cope with the quantity of water flowing through the system at this time. Consequently, the contents of the system will overflow at gullies or even at sanitary appliances inside the building.

## Slide 4: Combined system

## Slide 5: Separate system
An improvement on the combined system is the separate system.
In this system, the wastewater is conveyed in foul drains and sewers and the surface water is conveyed in separate surface water drains and sewers. As the name implies, both waste water and surface water are kept completely separate throughout.
The problems outlined above are overcome as only waste water is conveyed to the sewage treatment plant and the surface water is conveyed into watercourses, such as burns, streams, rivers, etc. via a surface water sewer.

## Slide 6: Separate system

## Slide 7: Partially separate system
This is a compromise system in which two separate networks are provided, one carrying storm water and the other foul water, plus the storm water off house roofs and backyards. This has the merit of providing for a flushing of the foul sewer by the roof water, etc. each time it rains.
To allow for very exceptional periods of rainfall, the foul sewer must be provided with storm overflows, but they very seldom come into use. The possibility of pollution of watercourses remains, and the system is not favoured when compared with the totally separate one.

## Slide 8: Means of access
Access is required to drainage installations for testing, inspection and removal of debris. Access to drainage allowing rodding in both directions can be provided by inspection chambers, manholes and other access fittings.
Rodding eyes provide access for clearance of debris in the direction of flow only and should thus be used in conjunction with an access chamber or manhole at a point downstream.
No part of the drain or sewer should be more than 50m away from a manhole. The distance between points should therefore not exceed 100m.

## Slide 9: Ventilation
All drainage and sewerage systems require adequate ventilation to the open air in order to reduce the build up of toxic or explosive gases and to maintain atmospheric pressure when effluent flows through the drainage system.
Ventilation should be provided at the head of a drain, normally through a soil and vent pipe or separate vent stack, but not through a manhole.
Gullies incorporated in a foul water or combined drainage system must have a 50mm minimum water seal.

## Slide 10: Good drainage practice
The drainage layout should be as simple and direct as possible.
Materials used should be hard, smooth non-corrosive and in true shape.
Pipes should be laid to falls to give a self-cleansing velocity.
This is generally considered to be: for a 100mm pipe to have a fall of 1 in 40, a 150mm pipe a fall of 1 in 60 and a 225mm pipe to have a fall of 1 in 90.
All joints must be airtight, watertight and free from internal obstruction.

## Slide 11
Any questions?