## Slide 1: PowerPoint 2: Copper pipework and jointing part 1
PowerPoint presentation
Unit 113: Plumbing, heating and ventilation

## Slide 2: This session:
In this session we will learn about the grades of copper pipe used within BSE and some of the methods used to joint it:
2.1 – The work in the BSE occupations trade area
2.2 – How to select and safely use hand tools and power tools
2.3 – The pipework materials and sizes used in BSE
2.5 – The fitting types used in BSE

## Slide 3: Grades of copper pipe
Mini-bore/microbore: 6, 8, 10mm
Small bore: 12, 15, 22mm
Large bore: 28mm and larger
When copper is purchased the half-hard copper R250 can be bought in 3m or 6m straight lengths. Soft mini-bore R220 copper is bought in coils of either 10m or 50m.
Old BS2871 | New BSEN1057 | Type | Diameters (mm)
Table W | R220 | Coiled micro-bore (heating) | 6, 8, 10
Table X | R250 | Half hard straight lengths | 15–54 domestic 6, 3, 2, 1 metre lengths
Table Y | R220 | Annealed coils for underground | 15–22 underground 25 metre lengths
Table Z | (R290) | Hard thin walled | Not commonly available now

## Slide 4: Grades of copper pipe
 | Gas (natural)
 | Water (other)
 | Central Heating
 | Water (Wholesome)
 | Chrome decorative
Protecting copper pipe is important in vulnerable areas and can be achieved by wrapping with denso tape or by using factory sheathed copper pipe. Copper is most vulnerable when laid in concrete flooring and when it emerges from the floor.
Some copper pipe is manufactured with a protective coating to protect against corrosion. In this case it can be colour-coded as shown below:
Notes: Look at the Yorkshire copper website here for more information

## Slide 5: Jointing copper pipe – compression joints
Type A: non-manipulative fitting
Requires the piece of pipe to be cut square and the burrs removed.
The fitting is assembled with an olive and tightened using an adjustable spanner.
Suitable for half-hard copper and plastic pressure pipe.
Backnut Compression ring Fitting body Tube

## Slide 6: Jointing copper pipe – compression joints
No matter what type of joint, fittings are available in a variety of arrangements and orientations including:
Elbows – 90 and 45 degrees
Tees – both equal and reducing
Couplings and sockets for straight joints
Reducers – internal and external reducers to change the pipe diameter
End caps and plugs – to make safe open pipes
Elbows Tees Couplings Reducers End caps

## Slide 7: Jointing copper pipe – compression joints
Type B: manipulative fittings
Require the end of the pipe to be manipulated using a swaging tool.
Much stronger than Type A fittings and cannot be pulled apart.
Mostly used for high pressure and below-ground pipe work.
Tube Swaged end of tube Adaptor Fitting body Tube
Swaging tool or drift

## Slide 8: Jointing copper pipe – compression joints
Type B: manipulative fittings
Step 1 – Cut and deburr the tube. Slip the compression nut and the compensating ring over the tube and flare open the end.
Step 2 – Insert the parallel end of the adaptor piece into the fitting socket and position the flared end of the copper tube over the tapered face of the adapter piece.
Step 3 – Screw the compression nut and ring onto the fitting body by hand and then tighten with a spanner. One full turn should be sufficient.

## Slide 9: Copper pipe jointing – push fit joints
These components are produced by many manufacturers and come in different finishes.
Grab ring
Fitting body
Tube insertion
O ring

## Slide 10: Jointing copper pipe – push fit joints
Can be used on pressure plastic pipe or copper pipe.
Pipe end must be cut square and burr free.
Sleeve or insert used to support plastic pipe.
‘O’ ring creates watertight seal.
Grab ring retains pipe.
Silicon gel can be used to aid insertion (manufacturers supply fittings already lubricated).
A key or release tool may have to be used to remove fitting.
Reusable.

## Slide 11: Jointing copper pipe – push-fit joints
These brass ‘Tectite’ style fittings are also push-fit and are a more
aesthetic way of jointing copper pipes by the push-fit method.

## Slide 12
Any questions?