## Slide 1: PowerPoint 22: Hydronic heating part 7
PowerPoint presentation
Unit 113: Plumbing, heating and ventilation

## Slide 2: This session:
In this session we will look at the range of heat emitters available for both domestic and I&C applications.
1.6 – The types and layout features of heating systems
What is a heat emitter?
The heat emitter is the final component in the system. It is the part of the system that exchanges the heat from the water within the hydronic heating system into the space that we need to heat. Therefore, the Heat Emitter is a heat exchanger suitable for the particular space!
Heat may be exchanged by radiation, convection or conduction.

## Slide 3: Heat emitters – panel radiators
These are the modern radiators found in new-build properties.
Approximately 70% of the heat is convected, via the fins welded to the back of the radiator.
They heat the cold air that passes over them, creating convection currents. Radiators that do not have fins rely heavily on radiated heat, which can result in cold areas in the room.
Manufacturers recommend that they should be fitted at least 150mm from floor height, (depending on skirting height).
Single panel
Single panel single convector fins
Double panel single convector fins
Double panel double convector fins

## Slide 4: Heat emitters – panel radiators
Seam top: commonly found, top and side grills available
Manufacturers supply many heights of radiator: 300–900mm. They also supply varying lengths from 400mm (increasing by 100mm).
Compact: most common, grills are factory fitted
Rolled top: Least popular, older type

## Slide 5: Heat emitters – panel radiators
The radiators are connected to the pipework in various ways:
TBOE: Top – Bottom – Opposite Ends. This is the most efficient way to pipe radiators. Not recommended for copper connections, but fine for LCS.
BBOE: Bottom – Bottom – Opposite Ends. This is the usual and most common method to pipe radiators, showing little pipework.
TBSE: Top – Bottom – Same End. Rarely found except on some one-pipe systems.

## Slide 6: Heat emitter – column radiators
Column radiators have been available for many years.
As the name suggests, they are made up of columns; the more columns the radiator has, the better the heat output.
They are increasingly being used with modern heating systems, especially on period refurbishments.
This type of radiator was often installed in older hospitals … can you think why?
Because they are easy to keep clean compared to panel type radiators.

## Slide 7: Heat emitter – low surface temperature radiators
LSTs were originally designed for the NHS, where radiators couldn’t have a surface temperature above 430C.
This was then accepted by nurseries, primary schools and homes for the elderly, disabled or infirm.
The HSE suggests that heating devices should not exceed 430C when the system is running at maximum design output.
Notes: Look at this LST Installation video

## Slide 8: Heat emitters - fan convector / Fan Coil Unit (FCU)
A copper heat exchanger mounted in the casing has lots of fins attached. This allows for additional surface area.
Below this heat exchanger, a low volume electric fan is installed, which is operated by the heat exchanger warming up.
These emitters can heat up large areas quickly.
Air drawn in by fan via air filter
Electric fan moves air over the heat exchanger
Heat exchanger transfers heat from water to air
Warm air out to space

## Slide 9: Heat emitters – fan convector / Fan Coil Unit (FCU)
FCUs are a very popular method of heating open plan office spaces where walls are not available internally for fixing radiators.
The units are fixed above the ceiling and have LTHW F&R connections for heat.
The heat is transferred to the air by a heat exchanger and a fan distributes this heat via ducts into the office space.
These units often have ‘chilled water’ connections for cooling in warmer periods.
Suspended Fan Coil Unit (FCU)

## Slide 10: Heat emitters – skirting convector
This type of heater also has a finned copper heat exchanger but relies on natural convection only.
It is installed around a room instead of skirting boards and offers background heating.
The main disadvantage with this type of emitter is that dust can block the fins and stall the convection current.

## Slide 11: Heat emitters – towel heaters
These are available in a wide range of designs and colours and can be used in a wet central heating system or independently with an electrical element.
Towel rails can come with an inverted radiator, conventional tubular style or designer styles.

## Slide 12: Heat emitters – radiant panel
Radiant panels are hygienic and aesthetically pleasing, with no visible heat emitters on show. They are often used in hospital installations where they are built into the ceiling and radiate heat downward.

## Slide 13
Any questions?