## Slide 1: PowerPoint 16: Hydronic heating part 1
PowerPoint presentation
Unit 113: Plumbing, heating and ventilation

## Slide 2: This session:
In this session we will introduce hydronic heating and the methods used to heat dwellings and buildings using wet systems.
1.6 – The types and layout features of heating systems
2.3 – The pipework materials and sizes used in BSE

## Slide 3: Central heating systems
The main purpose of central heating is to provide thermal comfort conditions within a building or dwelling. Central heating is preferable to open fires as it heats the whole property.
In a hydronic heating system, water is used to transfer heat from a boiler or heat generator to heat emitters throughout the building, such as radiators.

## Slide 4: Central heating systems
Domestic central heating systems fall into two categories. These are based on the way the system is filled with water and the pressure at which it operates. The two categories are:
Low-pressure, open-vented central heating systems, fed from a feed and expansion (F&E) cistern in the roof space. These can be both modern fully pumped systems and existing gravity hot water/ pumped heating installations.
Sealed, pressurised central heating systems, fed direct from the mains cold water supply and incorporating an expansion vessel to take up the expansion of water due to the water being heated. These are generally more modern fully pumped and combination boiler systems.

## Slide 5: Central heating systems
Domestic central heating system types can be classified by the sizes of tube they use, for example:
minibore – often called small bore, pipework sizes 15mm to 35mm
microbore – pipework sizes 8mm to 10mm.
The water in the heating system contains a chemical known as an inhibitor that prevents the metals in the system being corroded by the water.
The flow temperature of the water within the heating system is around 82⁰C depending on the system design.

## Slide 6: Generating the heat – domestic boilers
Heat is transferred into the water at the boiler. A huge range of boilers exist in both the domestic and I&C sectors. Unfortunately, we can’t cover them all here.
Here we will include the three main types of domestic boiler:
Combination boiler
Traditional boiler
System boiler
Wall hung combination boiler.
Floor standing traditional boiler.
Are there different types of domestic boilers? Look here.

## Slide 7: Generating heat – domestic boilers
Combination boiler
Ability to produce heat for the CH system and (when required) hot water for taps and outlets.
The most common type of boiler fitted in dwellings today and contains all the components within the boiler case.
Traditional boiler
Simplest type of boiler.
A heat source with a gas burner and heat exchanger, and minimum controls.
All other components of the CH system are external to the boiler, including the pump and the cylinder.
System boiler
Contains the controls and pump.
Unable to generate hot water by itself – needs a separate cylinder.

## Slide 8: Generating heat
Boilers can be fuelled by:
Natural gas
LPG (Liquid Petroleum Gas) such as propane
Fuel oil
Solid fuels such as biomass
Solid fuel ‘back boiler’.
Boilers can be further categorised by their efficiency (their ability to get as much heat as possible from the fuel).
Most modern boilers are high efficiency condensing boilers that operate at around 96% efficiency.

## Slide 9: Generating heat
So: what exactly is a boiler and how does it produce the heat?
A boiler is basically a heat exchanger where heat from the fuel is transferred from the hot gasses through the metallic heat exchanger into the water that is flowing through it.
Flow to system
Burner
Dry to wet heat exchanger
Return from system

## Slide 10: The one pipe heating system
This is an old and out of date method of installation, but a good place to start our understanding of what a hydronic heating system looks like.
15mm cold feed pipe
22mm vent pipe
Central heating circulating pump
Time clock
Boiler
28mm primary flow
28mm primary
return
Feed and expansion cistern

## Slide 11: The one pipe heating system
An obsolete system of which there are many still in existence.
The system uses a ring circuit of pipework to which both radiator connections are made.
It was usual with this system to fit a circulating pump on the return to the boiler.
Unlike modern systems, hot water temperature control and heating temperature control relied upon the boiler thermostat.
Did you notice this system also has a cistern, cold feed pipe and open vent pipe, just like the open vented hot water system?
The same principles apply here. In this case, the cistern is called the feed and expansion or F&E cistern.

## Slide 12: The one pipe heating system
These systems are often referred to as ‘gravity’ or ‘pumped’ systems because they incorporate old heating technology in the form of gravity circulation and forced circulation via a central heating circulating pump.
We can see here that the hot water cylinder is heated through gravity or convection.
But the heating circuit has a pump fitted. This system is sometimes referred to as semi-gravity.
15mm cold feed pipe
22mm vent pipe
Central heating circulating pump
Time clock
Boiler
28mm primary flow
28mm primary
return
Feed and expansion cistern

## Slide 13: The one pipe heating system
The circulating pump creates movement in the water through centrifugal force.
The pump pushes and pulls water through the system by creating a difference in pressure between outlet and inlet pump.
Most domestic circulating pumps have three speeds, which correspond to varying circulatory pressures, or heads.
Domestic circulating pumps have either a 6m or a 10m head, Commercial pumps have a much greater duty.
Let’s take a closer look here
Small Domestic pump.
Large industrial pump.

## Slide 14: Hydronic heating – one pipe system summary
Hydronic heating uses water in a closed loop, either cistern (F&E) or mains (sealed) fed.
Open vented systems require F&E, cold feed and expansion pipe and open vent pipe.
Flow temperature from the boiler is approximately 82⁰C (depending on system and boiler).
Domestic boilers – combination, traditional and system.
Boilers can be fueled by natural gas, LPG, oil or biomass.
One pipe system loses heat after each heat emitter.
Gravity circulation poor, modern systems are fully pumped.

## Slide 15: Hydronic heating – one pipe system summary
ADVANTAGES
DISADVANTAGES
Cheap to install because there is less pipework involved in the installation as compared to other heating systems.
The water in the system cools as it travels from one heat emitter to the next. If the same heat output is to be obtained, larger heat emitters are needed the further from the boiler they are situated and/or the greater the number of heat emitters that the water travels through.
The system tends to circulate water within the main pipework ring. Circulation within the heat emitters can only be induced by a difference in the density of the water entering and leaving the system (gravity circulation).
Uncontrolled heating of the primary circuit by the boiler leading to overheating of the domestic secondary hot water by the coil heat exchanger.
Constant boiler cycling even when the hot water and heating are up to temperature leads to wastage of fuel energy.
The system is not compliant with Building Regulations Document L and should be updated.
The boilers fitted to this type of system are only about 78 per cent efficient or lower.
Condensing-type boilers cannot be fitted to this type of installation because of the gravity circulation required by the hot water storage cylinder.
Boiler cycling
This happens when a heating system has reached temperature, and the boiler shuts down. A few minutes later the boiler will fire up again to top the temperature up as the system loses heat, and after a few seconds shuts down again. This constant firing up and shutting down as the system water cools slightly wastes a lot of fuel energy.

## Slide 16
Any questions?