## Slide 1: PowerPoint 14: Hot water part 4
PowerPoint presentation
Unit 113: Plumbing, heating and ventilation

## Slide 2: This session:
In this session we will look at the basic principles of the unvented hot water system. This topic is covered further at higher levels of the qualification.
1.5 – The types and layout features of hot water systems
Note: It is a requirement that anyone who installs or maintains an unvented hot water storage system is competent to do so.

## Slide 3: Unvented hot water cylinders
Unvented hot water systems do not have an open vent pipe and are at higher pressure.
This means that they are potentially more dangerous than open vented systems!
The explosive effects of a defective unvented cylinder as it flashes to steam are that buildings are demolished in much the same way as a gas explosion!

## Slide 4: Unvented hot water cylinders
They operate under mains pressure, so are known as high pressure systems. This also means they do not require a CWSC in the loft.
These cylinders and systems do not have an open vent. This means the safety relief must be incorporated elsewhere in the system.

## Slide 5: Unvented hot water systems
Isolation valve __
In-line strainer
Pressure-reducing valve ___
Balanced cold connection
Single check valve _______
Tundish
The cold supply must be connected after the pressure-reducing valve, but before the single check valve on the unit, to ensure equal hot and cold pressures.
Expansion vessel
Expansion relief valve Temperature relief valve
Mains cold water supply
Discharge pipework

## Slide 6: Unvented hot water systems
These systems have no cistern and therefore need another method to accommodate expanded water as it heats up.
In this case, we use an expansion vessel. This contains a rubber membrane charged with air that the expanded water compresses as it expands.
Commercial gas fired unvented hot water storage vessel with expansion vessel shown on the right

## Slide 7: Unvented hot water systems
The hot and cold supplies are fed directly from the mains cold water supply via a pressure-reducing valve that reduces the pressure of the water to the operating pressure of the unvented hot water storage cylinder. The obvious advantages of this are:
Large amount of water that can be delivered to the shower head
Force of the water leaving the shower head, giving a powerful shower
No need for a CWSC

## Slide 8: Requirements
The cylinder must be fitted with a range of safety (temperature) controls so the hot water never reaches 1000C.
The discharge pipes are located in a safe place, are metallic in construction and visible.
The system must be maintained by a competent person.
Installations must be notified to the Local Authority or self-certified (Competent Person Scheme).

## Slide 9: Temperature control
Safety item 1 | Control thermostat | Controls the water temperature and is set between 60–650C
Safety item 2 | High limit thermostat (energy cut off) | Non re-setting device that isolates the heat source when the water temperature reaches 80–850C
Safety item 3 | Temperature relief valve | This valve opens and discharges the contents of the cylinder when the water temperature reaches 90–950C

## Slide 10
Any questions?