## Slide 1: PowerPoint 3: Copper pipework and jointing part 2
PowerPoint presentation
Unit 113: Plumbing, heating and ventilation

## Slide 2: This session:
In this session we will learn about other methods available to join copper pipe:
2.1 – The work in the BSE occupations trade area
2.2 – How to select and safely use hand tools and power tools
2.3 – The pipework materials and sizes used in BSE
2.5 – The fitting types used in BSE

## Slide 3: Copper pipe jointing – press-fit
Press-fit fittings are available in all standard sizes, just like compression and push fittings … see here how the process is carried out.
Press-fit fittings rely on an ‘O’ ring to create the watertight seal
They are pushed into position after marking the component depth
Once in place, they are clamped in position using a mechanical crimping tool
15mm press-fit equal tee

## Slide 4: Copper pipe jointing – press-fit
STEP 1 – Cut the tube, preferably with a tube cutter, and deburr the pipe. Care should be taken to ensure that the tube is cut square.
STEP 2 – The tube must be fully inserted into the socket. To ensure this, use a socket depth gauge to mark the depth of the socket onto the tube or, alternatively, measure and mark using a rule.

## Slide 5: Copper pipe jointing – press-fit
STEP 3 – Insert the tube into the fitting all the way to the tube stop. The fitting depth mark previously made on the tube will help as a guide.
STEP 4 – Place the jaws of the press-fit tool over the bead of the fitting, making sure that the jaws of the tool are well lubricated.

## Slide 6: Copper pipe jointing – press-fit
STEP 5 – A 90 angle between the tool and the socket must be maintained when making the joints.
STEP 6 – Press the trigger on the press-fit tool to start the jointing process, making sure that fingers are kept away from the jaws.

## Slide 7: Copper pipe jointing – capillary joints
Capillary jointing has been the traditional way of jointing copper pipe for some time, but now – particularly on larger construction sites – this is becoming less popular. See if you can guess why before the end of this presentation!
Capillary fittings use the principle of capillary action to draw solder into the fitting when they are heated by a blowtorch. There are two different types:
Integral solder ring
End feed

## Slide 8: Copper pipe jointing – capillary joints
Step 1 – Cut and deburr the pipe.
Step 2 – Clean the end of the tube and the inside of the fitting with steel wool or cleaning pad.
Step 3 – Apply flux to end of tube only, not to the inside of the fitting. Insert tube into the fitting, twist tube slightly when inserting. This ensures an even spread of flux. Clean any excess flux from outside the tube immediately with a dry cloth.

## Slide 9: Copper pipe jointing – capillary joints
Step 4 – Apply heat evenly to fitting and wait for 10 seconds. If the fitting is an integral soldered ring type, then solder will appear at the mouth of the fitting.
Step 5 – If fitting is an end feed type, then apply solder wire equivalent to half the diameter of the pipe (for 22mm, apply 11mm of solder wire) to the mouth of the fitting, ensuring that solder flows all around the socket.
Do not use too much heat or the fitting and flux will turn black and the fitting will not solder.
Step 6 – When the fitting has cooled down a little, clean off any excess flux with a damp cloth.

## Slide 10: Copper pipe jointing – capillary joints
Integral solder ring – This type of fitting has a band of lead-free solder housed inside a raised ring on the fitting socket and so extra solder is not needed.

## Slide 11: Fitting orders
When ordering tees with a mixture of end and branch sizes, care should be taken to ensure that the correct configuration is quoted.
The method to use when ordering tees is to quote the largest end, then the smallest end, and the branch last.
In the photograph, the tee would be ordered as:
(1) 22mm × (2) 22mm × (3) 15mm

## Slide 12: Fitting orders
The correct order of branches is important if you need to order reducing tees such as those pictured here.
Reduced end | Reduced branch | Reduced end and branch | Two reduced ends (pendant tees)
One end is reduced | Branch is reduced | One end and branch are reduced | Both ends are reduced

## Slide 13: And finally…
Have you figured why the use of capillary type fittings has become less popular on large-scale construction sites?
The use of flames on site is often restricted.
There is far more risk of fire when soldering, brazing and welding activities take place, therefore contractors and clients are looking at alternative technologies such as press-fit to reduce the risk.

## Slide 14
Any questions?