## Slide 1: PowerPoint 19: Hydronic heating part 4
PowerPoint presentation
Unit 113: Plumbing, heating and ventilation

## Slide 2: This session:
In this session we will discuss the differences between open vented and sealed heating systems.
1.6 – The types and layout features of heating systems

## Slide 3: Quick refresher
Task: Let’s start by sketching a simple open vented heating system. Include the major components needed to fill and keep the system safe.
You may have drawn something similar to this. This is a small domestic system, but – as we have discussed – the principles remain the same whether domestic or commercial.
22mm vent pipe
Feed and expansion cistern
Boiler

## Slide 4: Quick refresher: roles of the major components within an open vented system
Feed and expansion cistern: Provides static pressure in the system, keeps the system topped up when required and offers space for expansion as the water warms.
Open vent pipe: Keeps the system at atmospheric pressure, allows air to be removed and is a safety vent for excess pressure.
Cold feed and expansion pipe: Allows water to enter the system and allows expansion to reach the feed and expansion cistern as the water warms.

## Slide 5: The sealed heating system
Sealed heating systems are those that do not contain an F&E cistern.
They are filled with water directly from the mains cold water supply via a temporary filling loop.
The expansion of water is taken up by the use of an expansion vessel and the open vent is replaced by a pressure relief valve.
The system is usually pressurised to around 1 bar.
Any fully pumped heating system can be sealed, whether large scale I&C systems or small domestic systems. In fact, a combination boiler is a sealed system.

## Slide 6: Roles of the components – a comparison
In a sealed pressurised system, the F&E cistern and open vent are removed. Let’s look at how these roles are replaced.
Any excess pressure is now released by a pressure relief valve instead of the open vent pipe.
Head pressure is now provided by the pressure of mains via a filling loop, this replaces the cold feed pipe also.
Expansion is no longer taken up in the F&E cistern, instead it is accommodated in the expansion vessel.
Open vent pipe

## Slide 7: Sealed system – expansion vessel
Hot water expands increasing the system pressure
Schrader-type pressure valve for checking and topping up the air charge
Screwed male thread connection point to central heating system
Cold water at 1 bar pressure
Air at 1 bar pressure
Air at 1 bar pressure
1. When the system has no water in it, the diaphragm is pressed against the wall of the expansion vessel by the charge of air in it.
1. As the system heats up, the water expands and forces its way further into the expansion vessel increasing the pressure to around 1.5 bar and compressing the air charge behind the diaphragm to
1.5 bar.
2. When the system is filled with cold water, the water forces its way in slightly compressing the diaphragm. The water pressure is topped up to 1 bar

## Slide 8: Sealed system – with external expansion vessel
This domestic system is filled by mains pressure by a temporary filling loop, which should be disconnected once filled.
Expansion vessel
Pressure gauge
Pressure relief valve
Wiring centre
Programmer
Temporary filling loop with double check valve arrangement

## Slide 9: Sealed system – combination boilers
This combination boiler is shown with an external filling loop, but some have internal systems. You can see that the expansion vessel is fitted internally within the boiler.
Room thermostat
Time clock
Mains cold water
Combination boiler Expansion vessel
Pressure relief valve and discharge pipe
Heating flow
Hot water supply
Filling loop
Heating return

## Slide 10: Commercial sealed systems
Larger systems require potentially higher pressures to maintain the water level even at its highest points. Therefore they are often fitted with ‘pressurisation units’.
Pumps used to push water into the system to the required pressure
Cistern used to ‘break’ the mains water from the system water feeding the pumps
Mains cold water inlet
Cistern overflow outlet
Pressurised outlets to system
Electronic controls

## Slide 11: Commercial sealed systems
Much larger expansion vessels are required for larger I&C systems. The more water the system holds, the more expansion takes place!
System water from the heating system is taken in the top part of the vessel.
The rubber diaphragm separates the water from the gas section and allows expansion.
Air or nitrogen is pressurised in the lower section, allowing the diaphragm to expand into it.

## Slide 12: High temperature systems
Some I&C systems can operate at over 150⁰C. This means the water is still water at that temperature! Does anyone know how this is possible?
By pressurising! The boiling point of water increases as the pressure increases.
For example, if water in a vessel is pressurised to 5 bar (5 x atmospheric pressure), the boiling point of that water is raised to approximately 150⁰C.
Some large heating systems and industrial processes use this principle to allow more heat energy to be put into the water. This is achieved by using pressurisation units and relevant controls.

## Slide 13
Any questions?