## Slide 1: PowerPoint 13: Hot water part 3
PowerPoint presentation
Unit 113: Plumbing, heating and ventilation

## Slide 2: This session:
In this session we will look at localised and instantaneous hot water and also how secondary hot water circuits are used:
1.5 – The types and layout features of hot water systems

## Slide 3: Instantaneous hot water systems
This type of appliance heats the water straight from the water main and only operates as long as the water is flowing.
It has no hot water storage. There are two different types:
Over sink
Under sink
These appliances can be further categorised as:
Simple hand wash heaters
Electric showers
Vented under-sink water heaters
Unvented under-sink water heaters (discussed later)
Note: In general, a storage unit is classed as containing more than 15 litres.

## Slide 4: Multi-point heater
Cold water is taken from the water undertaker’s main and heated in a heat exchanger before being distributed to the outlets.
As long as the tap is running, hot water will be delivered to the taps.
There is no storage capacity.
These heaters tend to have a good flow rate, meaning they can feed more than one tap or outlet.
Rinnai water heater video.
Heat exchanger
Combustion chamber
Cold water inlet
Hot water outlet
Thermocoupling
Pilot flame
Gas inlet
Burner
Push rod Venturi tube
Diaphragm
Pressure differential valve

## Slide 5: Combination boilers
Combi boilers provide instantaneous hot water and central heating within the same appliance.
In normal working mode, combination boilers are central heating appliances, supplying a proportion of their available heat capacity to heat the central heating water.
When a hot tap is opened, a diverter valve diverts boiler water around a second heat exchanger, which heats cold water from the water undertaker’s cold water mains to supply hot water at the hot taps.
Central heating flow and return
System bypass
Combustion air in
Water-to-water heat exchanger
Diverter valve
Gas
Cold Hot
water water
inlet outlet
Pressure relief valve
Fully modulating multifunctional control
Primary heat exchanger Spark igniter
Gas burner
Combustion air in Flue gas outlet Combustion air in
Expansion
vessel
Pump
Automatic air valve
Pressure switch

## Slide 6: Localised water heaters
This type of heater is generally used to supply small quantities of hot water such as washbasins and showers.
Typical minimum water pressure is 1 bar.
It is usually sited above the sink but under-sink models are available.

## Slide 7: Vented under-sink water heater
These are fitted under the sink or wash basin rather than above it.
They are similar in design to the over-sink type, but they are installed with a special tap that allows inlet water control while still maintaining an open vent through the outlet of the tap (see diagram).
Hot water supply from the heater to the tap
Mains cold water supply to the tap
Cold water supply from the tap to the water heater
Undersink water heater
Spout of the tap acts as an open vent allowing expansion of water to take place

## Slide 8: Localised hot water summary
ADVANTAGES
DISADVANTAGES
Can only be used for single appliances
Poor hot water flow rates (instantaneous types)
Relatively cheap to buy and install
Can be used at almost any location (electric types)
Only small hot water storage capacity (storage types)

## Slide 9: Secondary circulation
Once the water is heated, the system needs to retain the heat and supply hot water effectively to the outlet on demand.
Heat loss is minimised by the use of insulation on the cylinder and pipework (Building Regulations part L).
We should minimise the length of potential dead legs in the hot water delivery pipework so that:
We can reduce the amount of colder water that is wasted before getting to the hotter water.
We can reduce the amount of hot water left stagnant after use which could lead to bacterial growth.

## Slide 10: Secondary circulation
To overcome a dead leg, localised hot water can be installed or the use of a secondary circulation should be used.
This allows the circuit of hot water to be much closer to the outlet point.
Bronze pump
Secondary return 1/4
of way down cylinder
Secondary return connection at the furthest appliance
Vent
Feed
22mm or 28mm full-way gate valve or lever type spherical ball valve

## Slide 11: Secondary circulation
Secondary circulation ensures that water does not lose excessive heat as it is distributed and that it does not become stagnant.
The temperatures of hot water should be kept at the following temperatures throughout the system:
Storage: 60–65⁰C
Distribution pipework: no less than 50⁰C at the furthest point within the system.

## Slide 12
Any questions?