## Slide 1: PowerPoint 11: Hot water part 1
PowerPoint presentation
Unit 113: Plumbing, heating and ventilation

## Slide 2: This session:
In this session we will introduce types of hot water systems available for domestic applications, including centralised, open vented and direct systems:
1.5 – The types and layout features of hot water systems

## Slide 3: Hot water systems
Hot water systems, whether in a domestic property or a large-scale commercial property, share many principles. The scale and control of these systems may change, but the operation is very similar. There is a huge range of methods to produce and distribute this hot water.
Instantaneous
Hot water supply
Centralised system
Localised or single-point system
Storage
Instantaneous
Thermal store
Combi boiler or
instantaneous water heater
Combined primary storage units
Gas-fired
Open-vented hot water heater
Unvented hot water heater
Electric
Unvented / mains-fed system
Gas storage water heater
Open-vented / cistern-fed system
Combination vented 'fortic' systems
Direct
Indirect
Indirect
Direct
Indirect
Direct
Small hot-water- only boiler
Immersion heater
Small hot-water- only boiler
Storage
Immersion heater

## Slide 4: Hot water systems: centralised versus localised
Centralised hot water systems, where hot water is delivered from a central point to all hot water outlets in the dwelling or Commercial property. These can be further divided into centralised storage hot water systems or centralised instantaneous hot water systems.
Localised hot water systems, often called single-point or point-of-use systems. Hot water is delivered by a small water heater at the point where it is needed.

## Slide 5: Centralised storage and instantaneous hot water
In this session we will focus on centralised systems, both storage and instantaneous. We will discuss others later.
There are two main types of centralised storage hot water systems:
Open vented systems – fed from a cistern in the roof space.
Unvented systems – fed directly from the cold water main (discussed later).

## Slide 6: Centralised open vented systems
In an open vented system, the water is fed from a storage cistern in the loft down to a cylinder where the cold water is heated to produce hot water.
The cistern provides the pressure through giving ‘static head’ or ‘head pressure’.
In this case, the cistern is 15m above the cylinder. This roughly converts to 1.5 bar of pressure at the base of the cylinder.

## Slide 7: Centralised open vented systems
22mm or 28mm cold feed to secondary hot water system
22mm or 28mm full-way gate valve or lever type spherical ball valve
22mm draw-off to the bath then reduced to15mm to all other appliances
22mm vent pipe discharging into the CWSC and sealed with a grommet
The open vented cylinder MUST have access to an open vent pipe that keeps the cylinder at atmospheric pressure, meaning the water cannot exceed 100⁰C!
Open vent pipe
Cold feed and expansion pipe
Hot water draw off to appliances and outlets

## Slide 8: Open vented direct hot water system – with boiler
Direct systems use a direct-type cylinder that is heated either by a small hot-water-only boiler or an immersion heater.
Because the water in the boiler comes directly from the hot water storage cylinder, the boiler must be made of a material that does not rust.
A direct hot water cylinder uses a hot-water-only boiler to heat the water and stores it in this cylinder.
Hot water draw-off connection 1" male thread
Immersion heater connection
Primary flow connection 1" female thread
The direct water cylinder does not contain any form of heat exchanger. The water in the cylinder is the same water that is in the boiler.
Alternative primary flow connection 1" female thread. Position depends on the manufacturer.
Primary return connection 1" female thread
Cold feed connection 1" male thread

## Slide 9: Open vented direct hot water system – with boiler
You can see in this image that the boiler warms the water that flows to the cylinder.
The hot water circulates from the boiler or circulator by the principle of convection. This is known as gravity circulation.
The hot water rises in the primary flow pipe, directly heating the stored water in the cylinder before the cooler water returns to the boiler.
22mm or 28mm full-way
gate valve or lever type spherical ball valve
22mm primary
circulating pipes
connect the heat sorce to the cylinder
22mm draw-off to the bath then reduced to15mm to all other appliances
Heat source. Gas circulator or back boiler behind a solid fuel fire
22mm vent pipe discharging into the CWSC and sealed with a grommet

## Slide 10: Open vented direct hot water system – immersion heater
One immersion heater is placed at the bottom of the cylinder to heat all the contents, and a second immersion heater is placed halfway down the cylinder for daytime top-up.
As an alternative to direct systems with a boiler, most modern direct systems use two 3kW immersion heaters placed in the side of the cylinder to heat the water.
The immersion heaters are wired to a time controller for use with cheaper-rate overnight electricity. The temperature of the immersion heaters is best limited to 55⁰C to ensure lower running costs and minimise scale build-up.

## Slide 11: Open vented direct hot water system – immersion heater
Most immersion heaters are rated at 3kW.
A kW (Kilo watt) is the measurement of heating power produced by the immersion heater.
A cylinder with a capacity of 120 litres heats up from cold to around 65⁰C in approximately 2 hours and a 210-litre storage cylinder heats up in approximately 4 hours.

## Slide 12: Open vented direct hot water system – immersion heater
The direct hot water system that uses an immersion heater does not need a boiler.
Alternatively, stand alone Gas fired hot water storage units can be used. These burn gas to produce the heat instead of an immersion heater.
22mm or 28mm cold feed to secondary hot water system
22mm or 28mm full-way gate valve or lever type spherical ball valve
22mm draw-off to the bath then reduced to15mm to all other appliances
Heat source. Top immersion heater for daytime top up. Bottom immersion heater heats up all the water in the cylinder via a daytime controller for the use of cheap rate over night electricity
22mm vent pipe discharging into the CWSC and sealed with a grommet

## Slide 13: Open vented centralised direct hot water - summary
Property size – suitable for most houses; generally only used in properties where there is no requirement for a wet central heating system (immersion heater only).
Storage capacity – varies with occupancy. Generally, 210 litres for four people.
Fuel type – mostly used with Economy 7 electricity, but can also be used with some solid fuel boilers and gas circulators. Gravity hot water circulation only.
Installation cost – the least expensive of all storage systems for houses when boilers and circulators are not fitted.
Fuel efficiency – Economy 7 electricity is 100% energy efficient. All the energy used goes into heating the water, but electricity cost can be high.

## Slide 14: Direct hot water pros and cons
ADVANTAGES
DISADVANTAGES
Quick heat-up time of water (both boiler and immersion- heater types)
Cheap to install
Risk of rusty water being drawn off at the taps if the wrong type of boiler is used (boiler only)
High risk of scale build-up in hard water areas if the water temperature exceeds 65°C (boiler only)
High risk of scalding because of the lack of thermostatic control (boiler only)

## Slide 15
Any questions?