## Slide 1: PowerPoint 12: Hot water part 2
PowerPoint presentation
Unit 113: Plumbing, heating and ventilation

## Slide 2: This session:
In this session we will expand our understanding of the range of hot water systems used in domestic dwellings, this time looking at the principles of indirect hot water systems:
1.5 – The types and layout features of hot water systems
Although the details we look at here really focus on domestic systems, the principle is easily transferred to commercial system layout, which we will cover later.

## Slide 3: Centralised open vented indirect hot water systems
An indirect system uses an indirect-type hot water storage cylinder, of which there are two distinct types:
Double-feed indirect hot water storage cylinder
Single-feed self-venting indirect hot water storage cylinder
These storage cylinders are different from the direct type in that they contain heat exchangers to heat the secondary water. In this unit we will focus on double-feed cylinders.

## Slide 4: Double-feed indirect hot water storage systems
Very common system of heating water
Uses a copper heat exchanger coil inside the cylinder
Heats the water ‘indirectly’ by passing heating water (primary water from a boiler) through the copper coil to heat the water around it (secondary water)
Called double-feed as it has a cistern to feed water into the heating system (primary water) and another to feed the cylinder (secondary water)
Immersion heater connection
Primary flow connection 1" male thread
Primary return connection 1" male thread

## Slide 5: Double-feed indirect hot water system
The primary and secondary waters are kept separate by use of the copper coil within the cylinder and the two cisterns.
The cistern provides the static head to push the water out of the outlets.
The secondary water is heated by conduction.
The cold water cistern accommodates the expanded water as it heats.
22mm or 28mm cold feed to secondary hot water system
22mm or 28mm full-way gate valve or lever type spherical ball valve
22mm primary flow and return pipes from the boiler to the coil in the cylinder
Heat source. Gas, oil or solid fuel
22mm draw-off to the bath then reduced to 15mm to all other service
Feed and expansion cistern fitted with BS1212 part 2 float-operated valve
Spherical ball type service valve
15mm cold feed to the primary system
Spherical ball type
service valve
22mm vent from primary hot water system connected to the boiler, the coil in the hot water cylinder and central heating system
150 litre storage cistern fitted with BS 1212 part 2 float-operated valve
22mm vent from secondary hot water system. To determine the height of the vent = 150mm + 40mm per metre of system height (m)
450mm

## Slide 6: Gravity and pumped circulation
Some older hot water and heating systems may rely on convection to allow water to flow between the boiler and the cylinder.
This is known as gravity circulation and is no longer installed.
This is inefficient and slow.
The Building Regulations now state that these ‘primary circuits’ should be fitted with a pump to allow the heat transfer to take place more efficiently.
Water circulating
without pump – gravity

## Slide 7: Gravity and pumped circulation
Modern indirect systems are fitted with a circulator on the primary circuit.
These primary circuit pipes are part of the heating system and carry heating water at around 82⁰C to exchange with the cold water to produce hot water at 60⁰C–65⁰C.
In this image you can see that the central heating and hot water are both controlled by motorised valves.
Central heating
flow and return
Water circulated via a pump or circulator

## Slide 8: Hot water control
The Building Regulations insist that there is adequate control of the hot water system to prevent the water reaching 100⁰C.
This is achieved by us of a cylinder thermostat and (in the case of an indirect cylinder) a two-port valve.
The water in the cylinder should be stored at 60–65⁰C.
OPEN

## Slide 9: Indirect double feed hot water system summary
Property size – suitable for all domestic properties when used with central heating systems.
Storage capacity – varies with occupancy. Generally, 210 litres for four people.
Fuel type – can be used with gas, oil, solid fuel, electricity and renewable energy fuel sources. Suitable for fully pumped heating systems. Conforms to Document L of the Building Regulations.
Installation cost – more expensive than direct systems due to the extra pipework for the feed and expansion cistern.
Fuel efficiency – gas and oil appliances must be energy-efficient condensing types. Can also be used with Economy 7 electricity.

## Slide 10: Indirect double feed hot water system summary
ADVANTAGES
DISADVANTAGES
Can be used with fully pumped heating systems and condensing boilers
Wide range of capacities available
Fully compliant with Document L of the Building Regulations
Expensive to install
Will require a second cistern and associated pipework or expansion vessel and
filling loop

## Slide 11
Any questions?