## Slide 1: PowerPoint 4: LCS pipework and jointing
PowerPoint presentation
Unit 113: Plumbing, heating and ventilation

## Slide 2: This session:
In this session we will learn about other methods available to join copper pipe:
2.1 – The work in the BSE occupations trade area
2.2 – How to select and safely use hand tools and power tools
2.3 – The pipework materials and sizes used in BSE
2.5 – The fitting types used in BSE

## Slide 3: Low carbon steel pipe
Low carbon steel (LCS) is a robust material often used in Industrial and Commercial applications and some large-scale Domestic applications for heating systems.
Must not be used for hot or cold water supplies for Domestic purposes because of the risk of rusty water being drawn from the taps.
Often referred to as mild steel pipe, low carbon steel pipe is usually supplied painted red or black.
Can also be galvanised. Its carbon content is low.

## Slide 4: Low carbon steel pipe
Low carbon steel pipe is available in three grades, each grade being identified by a colour code:
The grades of low carbon steel have identical external diameters, but the pipe’s wall thickness will vary according to the grade.
As the grade of pipe increases, the nominal bore (NB) of the pipe decreases, but the fittings used are the same for all grades.
Grade | Colour code
Light | Brown
Medium | Blue
Heavy | Red

## Slide 5: Low carbon steel pipe
Low carbon steel pipe is available in 6m lengths and may be supplied with threaded ends or plain ends. It is often still referred to by imperial pipe sizes, which are specified as nominal bore (NB).
Normally joined by screwed and socketed joint (British Standard Pipe thread - BSP), flanges or welding, although other technologies are being developed.
Press-fit can be used on specific thin wall carbon steel pipe: take a look here.
Thread / fitting size (in) | 1/8” | 1⁄4” | 3/8” | 1⁄2” | 3⁄4” | 1” | 11⁄4" | 11⁄2” | 2 “ | 2 ½” | 3” | 4” | 5” | 6” | 8”
Thread / fitting size (mm) | 6 | 8 | 10 | 15 | 20 | 25 | 32 | 40 | 50 | 65 | 75 | 100 | 125 | 150 | 200
Standard LCS sizes from 1/8” to 8”

## Slide 6: Threaded joints
Low carbon steel pipes can be jointed using threads to BS 21:1985, and BS EN 10226-1:2004, which are cut into the end of the pipes using either manual stocks and dies or electric threading machines.
There are two types of thread:
Parallel thread – usually used on internal threads such as fittings.
Tapered threads – cut onto the pipe ends. These tapered threads get tighter as they screw into the parallel fitting.
Threads remain parallel throughout the length of the tube
Threads taper towards the end of the tube

## Slide 7: Threaded joints
Couplings | Equal tees | Elbows | M/F elbows
Pitcher tees | Unions | Nipples | Bushes

## Slide 8: Jointing compounds
Linseed-oil-based compounds (boss white, hawk white and templars paste) | Can be used in conjunction with hemp on wet central heating systems and compressed air lines. Must not be used on natural gas installations.
Unsintered polytetrafluroethylene (PTFE tape) | A thin, white (or thicker, yellow-sleeved if used on gas) tape that can be used on most installations, including hot and cold water, central heating and gas installations.
PTFE-based jointing compounds (boss green) | A compound specially made for use on hot and cold water supplies. Not suitable for natural gas installations.
Heldite paste | A universal compound that can be used on many installation types such as oil, gas, hot and cold water, central heating, compressed air lines and vacuum lines. It is not suitable for potable water supplies.
Manganese paste | These are specialist compounds for use with high temperature hot water and steam installations.
Graphite paste | 
Gas seal paste | A specialist compound for use with natural and liquid petroleum gas installations.

## Slide 9: Welded fittings and joints
In some cases, the welding of LCS pipe may be necessary – particularly in boiler room installations where multiple connections to headers are required.
Small boiler room with welded LCS branches from low loss header / manifold.
Weldable fittings are available in the same size as screwed fittings.
Welding processes for the installation of LCS pipe in BSE applications includes:
Manual Metal Arc (MMA)
Tungsten Inert Gas (TIG)
Oxy-Acetylene welding

## Slide 10: Welded fittings and joints
Pipe fitter pre-fabricating LCS pipework using the TIG process offsite to reduce the hot works onsite.
The MMA process is being used to weld this flange offsite before bolting up in position onsite.

## Slide 11: Jointing by flanges
Flanges, like unions, allow pipes to be disconnected when required. Flanges need to be fitted with a gasket to make the watertight seal between the metal surfaces.
Range of flange gaskets.
Flange on a heating pump allows the pump to be removed for maintenance and repair.

## Slide 12
Any questions?