## Slide 1: PowerPoint 10: Cold water systems in industrial and commercial premises
PowerPoint presentation
Unit 113: Plumbing, heating and ventilation

## Slide 2: This session:
In this session we will take a look at how the water that is supplied to an industrial or commercial property is distributed and used:
1.4 – The types and layout features of cold water systems
2.3 – The pipework materials and sizes used in BSE
Remember: The principle of cold water systems stays the same whether it’s a house, a school or an office block.
The layout may change slightly, but all work on cold water systems provided by the water supplier (the Water Undertaker) must comply with the correct regulations. In our case, that regulation is The Water Supply (Water Fittings) Regulations 1999.

## Slide 3: Industrial and commercial cold water supplies
What do you think might be the main differences between a domestic cold water system and an I&C cold water system?
Size – Typically a domestic supply is 25mm diameter, while an I&C supply may be anything from 25mm to 300mm.
Quantity – A domestic dwelling may require enough water for perhaps two WCs, a bath, two wash hand basins and a kitchen sink.
For example, a school may have dozens of bathrooms, large-scale kitchens, showers and laboratories. Hence the large pipe!

## Slide 4: Industrial and commercial cold water supplies
What do you think might be the main differences between a domestic cold water system and an I&C cold water system?
Pressure – To get water to heights requires pressure. In fact, to raise water 10m in height, a minimum pressure of 1 bar is needed!
This tower building in Swansea is 107m tall.
The tower building here is 107m tall. What pressure would be needed to get the water to its highest point?
Correct, 10.7 bar! Mains water is normally around 2.5 bar … so how do we get the water to the highest point? Let’s take a look.

## Slide 5: Boosted cold water systems
Boosted cold water is a method that can supply water to the highest part of the building. There are several ways this can be done, including:
direct boosting systems – which draw water directly from the cold water mains supply
the more popular indirect boosting systems – which draw from a break cistern.
Most water undertakers (suppliers) won’t allow direct boosting unless the amount of water being drawn is less than 0.2L/s!

## Slide 6: Direct boosted cold water
The pumps are controlled by a float switch inside the high-level cistern. The pumps either switch on or off depending on the water level in the cistern.
When the water drops to about half the cistern capacity, the pumps will be activated and will switch off again when the water level reaches a depth of about 50mm below the shut-off level of the float operated valve.
Pump stop
Pump start
Stop valve
Incoming supply
Duplicate pumps
NOTE: This drawing does not show any additional backflow prevention devices that may be required under the Water Supply (water fittings) Regulations 1999.

## Slide 7: Indirect boosted cold water
A break cistern is used to store the water before it is pumped via a boosting pump (a booster set).
The pumps are fitted to the outlet of the break cistern.
The water level in the cistern is controlled by water level switches that activate the pumps.
Pump stop
Pump start
Pump stop
Pump start
Filtered air vent
Incoming service
Pump stop
Pump start
Break cistern
Duplicate pumps
Overflow and filter

## Slide 8: Storage cisterns
Large commercial and industrial systems may incorporate cisterns. This may be:
break cistern – at the bottom of a boosted cold water installation, and/or
a storage cistern at the top of a building feeding the outlets by gravity.

## Slide 9: Industrial and commercial storage cisterns
Due to their size, I&C cisterns are often built in sections and are often constructed from Glass Reinforced Plastic (GRP), which is relatively light and strong.
Some older galvanised steel tanks are still in operation, but tend to rust over time, causing problems with water quality.

## Slide 10: Float operated valves
No matter whether the cistern is a domestic one or a large I&C cistern, it must be fitted with a device to control the level. Most commonly, this is done with a Float Operated Valve – FOV.
Copper float
Float arm
Water outlet
Flange gasket
Flange bolts
Water inlet
Flange
Piston

## Slide 11
Any questions?