## Slide 1: PowerPoint 9: Direct and indirect cold water systems
PowerPoint presentation
Unit 113: Plumbing, heating and ventilation

## Slide 2: This session:
In this session we will look at how the water which is supplied to a property is distributed and used:
1.4 – The types and layout features of cold water systems
2.3 – The pipework materials and sizes used in BSE

## Slide 3: Cold water system basics
In this session we will look at the systems we install within a property.
Each dwelling should have at least one ‘potable’ water supply outlet.
In the home this is normally the kitchen sink.
Drinking water must also be provided in areas of food preparation in other buildings like offices or commercial properties.
We can either connect outlets directly to the mains water supply or indirectly via a protected cold water storage cistern (CWSC).

## Slide 4: Water to the dwelling
When the water supply enters the property, it should terminate with a screw-down stop valve, a lever action, spherical plug valve or, on large installations, a flanged gate valve.
As you can see in the image, the water main enters the building underground.
This water main should be between 750mm and 1350mm below ground.
75mm service duct sealed at both ends No other service or cable in duct
150mm

## Slide 5: Direct cold water systems
All cold water taps are fed directly from the mains supply and are therefore potable.
Direct systems are the most common type of cold water system used in modern Domestic properties.
Relatively high pressure of supply available from the mains and it is a cost-effective installation.
Spherical ball type
service valve
WC cistern fitted with either a BS 1212 part 2
part 3 or part 4 float-
operated valve
15mm mains cold water to all appliances
Drain-off valves
22mm or 28mm cold feed
to secondary hot water cylinder
22mm or 28mm full-way gate valve or lever type spherical ball valve
100–150 litre storage cistern fitted with BS 1212 part 2 float-operated valve
Spherical ball type
service valve

## Slide 6: Direct cold water systems
Storage only required for supplying cold water to the hot water cylinder, typically via a 150-litre cistern.
Feed cistern not necessary if the hot water is supplied via an instantaneous hot water heater or ‘combi’ boiler, unless incoming pressure is unusually low.
Both hot and cold water supplies are now fed directly from the mains.
Drain-off valves
Spherical ball type
service valve
No water pipes or cisterns in the roof space. No risk of burst pipes due to freezing
WC cistern fitted with either a BS 1212 part 2 part 3 or part 4 float-operated valve
15mm mains cold water to all appliances
Appliance off the cold water mains

## Slide 7: Direct system
Pipe sizes for a direct system really depend on the system’s design and number of outlets, but generally speaking:
15mm rising main will be large enough to supply most cold water demands for a three-to-four bedroom home with all cold water outlets being supplied in 15mm, including the bath.
If a hot water storage cylinder is installed, a 28mm cold feed is required to the cylinder from a 150-litre cold water storage cistern.
Larger installations may require a 22mm rising main, but this is dependant again on the system requirements.

## Slide 8: Indirect systems
In the indirect system, the cold water main feeds the outlets indirectly via a cold water storage cistern.
The cold main connects first to the cistern in the roof space before feeding out of the cistern to the outlets.
All properties should have at least one outlet connected directly to the main for drinking water, therefore the kitchen sink is directly fed.
Spherical ball type
service valve
WC cistern fitted with either a BS 1212 part 2
part 3 or part 4 float-
operated valve
22mm cold distribution pipework to the bath reducing to 15mm to feed the wash hand basin and WC cistern
Drain-off valves
22mm or 28mm cold feed to secondary hot water cylinder
22mm or 28mm full way gate valve or lever type spherical ball valve
230–250 litre storage cistern fitted with BS 1212 part 2 float-operated valve
Spherical ball type
service valve

## Slide 9: Indirect systems
Notice that the kitchen is fed directly from the main.

## Slide 10: Making second fix connections
All appliances, whether a bath, wash hand basin or dishwasher, must be provided with means of isolation. A slotted ball valve or service valve is most suitable.
Flexes for WC and wash hand basin connections may have built in service valves or they may be installed separately on rigid pipework.
Dishwashers and washing machine valves must also be provided with isolation.

## Slide 11: Making second fix connections
Washbasins are usually connected with 15mm pipe, but many new monobloc washbasin taps have 10mm connections.
10mm pipe should be restricted to the last 1m of pipework, otherwise the flow rates required may be affected.
Flexible connections are an alternative, although their use may be restricted in some healthcare facilities due to tightened restrictions concerning contamination.

## Slide 12
Any questions?