## Slide 1: PowerPoint 15: Hot water part 5
PowerPoint presentation
Unit 113: Plumbing, heating and ventilation

## Slide 2: This session:
In this session we will discuss the methods used to generate hot water within I&C buildings.
1.5 – The types and layout features of hot water systems

## Slide 3: Industrial and commercial hot water systems
No matter what the scale, hot water systems still operate under the same principles and may be:
Vented or unvented
Storage or instantaneous
Localised or centralised
Direct or indirect
Electrically, gas, oil, or solar heated
Let’s take a look at some of the differences between I&C systems and the Domestic systems we have already discussed.

## Slide 4: ‘Domestic’ services
This does NOT refer to a system in a dwelling! It is a term used in I&C buildings.
The term DHW comes from the cleaning and facilities teams within hospitals, who are often known as domestic services assistants.
So… DHW systems are I&C hot water systems, NOT those in your home!
A common term used in I&C applications is ‘Domestic’ services or Domestic Hot Water (DHW) System.

## Slide 5: Indirect storage calorifier
A calorifier is basically a large hot water cylinder. It may be described as either a storage or non-storage type. Normally storage calorifiers are used for hot water systems and non-storage are used in heating systems to transfer heat from high temperature systems to low temperature.
Non-storage calorifiers are normally mounted horizontally.
Storage calorifiers are mounted vertically.

## Slide 6: Gas fired hot water heater
A common solution in I&C buildings are gas fired hot water heaters. These can store and deliver relatively large quantities of water and can be positioned locally where needed, providing a gas supply is available.
The heater has a gas burner fitted that heats the metallic heat exchanger surface in the vessel, which in turn heats the water.
Gas supply to burner
Notes: Take a look here.

## Slide 7: Indirect storage calorifier
Just like a domestic cylinder, vertical mountings ensure that stratification of hot water takes place with the hottest being at the top.
Stratification: The natural layering of hot air or water. As water or air is heated, it becomes less dense and rises to the top, whereas the colder denser water falls to the bottom!
Indirect hot water calorifiers are normally used in larger centralised plant rooms.
Hottest water at a max. temperature of 65˚C is at the top of the cylinder
Hot water at a max. temperature of 40˚C is at the bottom of the cylinder

## Slide 8: Gas fired hot water heater
Gas fired equipment such as these require:
Gas supply
Adequate ventilation
A suitable flueing system
Cold feed
Hot draw-off
Thermostat
Gas valve
Gas burner
Flue pipe

## Slide 9: Plate heat exchangers
A non-storage and efficient method of generating hot water.
A Plate Heat Exchanger (PHE) uses multiple stainless steel sheets to separate primary and secondary waters.
This prevents water mixing, but allows efficient heat exchange.

## Slide 10: Plate heat exchangers
PHEs are space saving and efficient methods of producing hot water. They are also used in conjunction with other systems and small versions can even be found in Domestic combination boilers to produce hot water and in thermal store units as shown in the diagram.
Notes: Plate heat exchanger video.

## Slide 11
Any questions?