## Slide 1: PowerPoint 6: Bending metallic pipe
PowerPoint presentation
Unit 113: Plumbing, heating and ventilation

## Slide 2: This session:
In this session we will learn about other methods available to bend metallic pipe:
2.1 – The work in the BSE occupations trade area
2.2 – How to select and safely use hand tools and power tools
2.6 – Common fixing devices for pipework
3.1 – How to measure and mark out for fixings to pipework and plumbing and heating components
3.2 – The sources of information for carrying out preparatory work
3.4 – The methods for the bending of pipework used in BSE
3.5 – The requirements for the installation of pipework

## Slide 3: Bending copper tube
Soft coils (R220 Table Y) and half-hard (R250 Table X) copper tube can be bent by using:
    Bending springs (internal or external)
    Hand bender (micro and small bore)
    Machine floor-standing bender (max 42mm)
Can you think of any advantages to bending pipe rather than using a fitting?
    Less frictional resistance
    Costs less
    Sections can be prefabricated in one go

## Slide 4: Bending copper tube – bends
900, 450
Offset
Back to back
Half pass over (kick over)
Full pass over

## Slide 5: Bending copper tube – spring bending
Internal and external bending springs are not used much today. They are occasionally used by plumbers when trying to bend an existing piece of pipe without creasing it.
Internal spring
External spring

## Slide 6: Bending copper tube – spring bending
The spring is tightened by twisting a bar through the end of the spring.
The spring bend is normally over-pulled and then eased back to 900 to make spring withdrawal easier.

## Slide 7: Bending copper tube
All bends appear to gain material on one side and compress material on the other side.
It is possible to accurately work out the length of pipe to be bent in relation to fixed points, by finding out the length of pipe the bend actually occupies.

## Slide 8: Bending copper tube
The radius centre line is normally four times the diameter of the pipe (4D).
Radius x 2 x 3.14
4
Can someone explain what the ‘radius’ is and what a ‘diameter’ is?
The radius of a circle or a bend is from the centre to the edge … or half of the diameter, which is from edge to edge!

## Slide 9: Bending copper tube – example
300mm
150mm
Radius 60mm
Work out the overall length of pipe.
Radius x 2 x 3.14
4
60 x 2 x 3.14
4
= 94.2mm
94 + 300 + 150 = 544mm

## Slide 10: Bending copper tube
22.50
450
900

## Slide 11: Bending copper tube – golden rules
Where possible, work from a fixed point to avoid cutting to length. The fixed, measured point always goes away from you when in the bender – waste to waist.
Mark the throat of the bend and select measuring method:
Back to back
Centre to centre
Back to inside
Inside to back
Measure twice, cut once or bend once! If a section needs two or three bends, make sure the first bend is correctly positioned in the bender before pulling the second. Take a look at the process here.

## Slide 12: Bending copper tube – tools
Scissor type bender and slips
Combination square
Engineer’s square
Steel rule (mm)
Pencil
Senior/junior hacksaw 32tpi

## Slide 13: Measuring and bending LCS tube – bends
900, 450
Offset
Half pass over (kick over)
Nowadays, commercial LCS is commonly fabricated using fittings rather than bending.

## Slide 14: Measuring and bending LCS tube
Pump handle
Air inlet
Hydraulic cylinder
Location lugs
Stops
Ram head
The frame

## Slide 15: Measuring and bending LCS tube – golden rules
When bending LCS pipe it stretches in both directions. LCS pipe stretches by its nominal bore:
½” = 15mm ¾” = 20mm
Level the hydraulic bender when doing multiple bends
Set stops in correct position
Use correct size on ram head
Allow for springback after pulling a bend – one full pump
Take a look at the process here.

## Slide 16: Measuring and bending LCS tube – tools
Hydraulic bender
Boat level
Combination square
Senior hack saw 24tpi
Engineer’s square
Steel rule
Frame square
Pencil

## Slide 17
Any questions?