## Slide 1
PowerPoint presentation
PowerPoint 7: The main principles of standard circuits
Unit 114: Electrotechnical systems and equipment

## Slide 2: Overcurrent protection
An overcurrent occurs when the current exceeds the rated capacity of that circuit. Examples of overcurrent protective devices are circuit breakers and fuses protect circuit wiring from damage caused by overcurrent.

## Slide 3: Re-wireable fuses
      A fuse is the weak link in a circuit which will ‘break’ when too much current flows, thus protecting the circuit conductors from damage.
The re-wireable fuse has a fuse wire held at both ends by a small retaining screw.

## Slide 4: Circuit breakers
A circuit breaker is an automatically operated electrical switch designed to protect an electrical circuit from damage caused by excess current from an overload or short circuit. Its basic function is to interrupt current flow after a fault is detected.
Unlike a fuse, which operates once and then must be replaced, a circuit breaker can be reset to resume normal operation.

## Slide 5: Residual current devices (RCD)
An RCD, or residual current device, is a device which is designed to prevent you from getting a fatal electric shock if you touch something live, such as a bare wire. An RCD is a sensitive safety device that switches off electricity automatically if there is a fault.
An RCD constantly monitors the electric current flowing through one or more circuits it is used to protect. If it detects electricity flowing down an unintended path, such as through a person who has touched a live part, the RCD will switch the circuit off very quickly, significantly reducing the risk of death or serious injury.

## Slide 6: Circuit requirements
Part of the wiring regulations from BS 7671 require that installations should be divided into circuits. This is to:
prevent danger in the event of a fault by ensuring that the fault current is no greater than necessary to operate the protective system.
enable part of an installation to be switched off for maintenance or for testing without affecting the rest of the system.
prevent a fault on one circuit resulting in the loss of the complete installation
The number of final circuits will depend on the types of load supplied. Every circuit must be separate from others and must be connected to its own overcurrent protective fuse or circuit breaker in a switch fuse, distribution board, consumer's unit.

## Slide 7: Older installations
The amount of electrical equipment used in households has dramatically increased. However, this wasn’t the case in old installations, and this is reflected in the wiring requirements. It is therefore very important that these installations are inspected and tested.

## Slide 8: Circuit overloading
If a circuit does not have a breaker, the insulation in the wiring could melt, and it could potentially start a fire. In most modern circuits, there are breakers in place.
If you overload a circuit, you are giving it too much work to handle. Each device you plug into a socket adds to a circuit’s overall load. If you exceed this load, a circuit breaker will operate and cut the power off.

## Slide 9: What are the signs of an overloaded circuit?
Complete loss of power in the home due to a protective device operating.
Burning sounds and smells from socket outlets
Hot or warm switches and sockets.
A burned or scorched switch or socket.

## Slide 10: Cable calculations
The purpose of performing a cable calculation is to ensure that a cable is not overloaded. This can produce an excessive amount of heat which in turn can damage the cable and the installation and may even cause a fire.
Some of the most common cables used are: 1mm² or 1.5 mm² for lighting circuits and 2.5mm² for socket-outlet circuits. However, those who undertake electrical installation work need to understand how to select the correct cross-sectional area of a cable for a particular use. Reference to the tables in Appendix 4 of BS 7671 and in Appendix 6 of the IET On-Site Guide will assist in cable calculations.

## Slide 11: Calculating the right size
A basic overview to calculating the right size of cable for a particular load are:
Calculate the design current (Ib). This is the normal current drawn by the load. It is usually determined as follows: Ib = Watts/ Volts
Select the type and current rating of the overcurrent device (In).

## Slide 12: Calculating the right size
Apply the relevant correction factors to obtain the tabulated current (It ). Correction factors are applied to situations which inhibit a cable from dissipating its heat caused by the normal flow of current through it. Therefore, shown below, are a few of the correction factors that may be applied:
  Ambient temperature, Ca
  Grouping, Cg
  Thermal insulation, Ci
  Re-wireable fuse (BS 3036) factor, Cf

## Slide 13: Calculating the right size
These correction factors are applied as divisors to the nominal current rating of the overcurrent protective device (In), to obtain the tabulated current (It). For example, in the worst possible situation where all four factors are applied, the formula would look like this:
It In_______ Ca x Cg x Ci x Cf

## Slide 14: Calculating the right size
When we obtain the tabulated current, we then have to calculate the voltage drop to ensure that it is not excessive.
Regulation 525-01-02 states that the voltage drop from the origin of the supply to the furthest point in the installation must not exceed four per cent of the supply voltage when the conductors are carrying full load current. The tables in Appendix 4 have a voltage drop section in which the millivolt per amp per metre (mv/a/m) of a particular cable may be obtained.
The voltage drop is calculated from:
Volts drop = mv/a/m x design current, Ib x length of run in metres
1000

## Slide 15: Calculating the right size
Further information and guidance on cable calculations will be given at level 3.
As stated earlier, the main source of information can be obtained from Appendix 4 of BS 7671, Protection against overcurrent, and for a more simplified approach, Appendix 6 of the IET On-Site Guide.

## Slide 16: Safety
In the UK, there is a vast amount of information set out to assist in the safe installation and testing of premises. The two main sources of information that assist the electrical installer are:
The Wiring Regulations (BS 7671) and
The IET On-Site Guide.

## Slide 17: Safety: The Wiring Regulations (BS 7671)
BS 7671 Wiring Regulations is the UK’s main electrical safety standard. It sets out the requirements that detail how to perform electrical installations safely.
It sets out regulations which apply to the design, erection and verification of electrical installations, and to additions and alterations to existing installations.
BS 7671 sets the standard for how electrical installations should be done in the UK and enables compliance with the law.
.

## Slide 18: Safety: The On-Site Guide
The On-Site Guide is designed to be taken on-site for easy referencing and provides simple guidance on the application of BS 7671.
The book is also relevant for students studying wiring-related courses. All expected updates to the new 18th Edition Wiring Regulations will be included in the On-Site Guide.

## Slide 19: Safety: earthing and protective conductors
Earthing is used to protect you from an electric shock. It does this by providing a path (a protective conductor) for a fault current to flow to earth. It also causes the protective device (either a circuit-breaker or fuse) to switch off the electric current to the circuit that has the fault.
There are different types of earthing and protective conductors used in electrical installation.

## Slide 20: Safety: earthing and protective conductors
Earthing conductor
The earthing conductor joins the installation earthing terminal to the earth electrode or to the earth terminal provided by the Electricity Supply Company. It is a vital link in the protective system, so care must be taken to see that its integrity will be preserved at all times.

## Slide 21: Safety: earthing and protective conductors
Circuit protective conductor
The circuit protective conductor (normally called the 'c.p.c.') is a system of conductors protecting individual circuits in an installation. They are all connected to the main earthing terminal.

## Slide 22: Safety: earthing and protective conductors
Bonding conductors
Equipotential bonding serves the purpose of ensuring that the earthed metalwork (exposed conductive parts) of the installation is connected to other metalwork (extraneous conductive parts) to ensure that no dangerous potential differences can occur.
Main protective bonding conductors These conductors connect together the installation earthing system and the metalwork of other services such as gas and water.

## Slide 23: Safety: earthing and protective conductors
Supplementary bonding conductors These conductors connect together extraneous conductive parts – that is, metalwork which is not associated with the electrical installation but which may provide a conducting path giving rise to shock.

## Slide 24: Safety: earthing and protective conductors
kWh meter
03117 3
kWh
Electricity company isolator
LABEL – Safety electrical
connection. Do not remove
LABEL – Safety electrical connection.
Do not remove
100 A
Main earthing terminal
16 mm2
10 mm2
10 mm2
16 mm2
Gas meter
Main switch
L
N N L
Metal gas pipe
Water service pipe
Gas service pipe

## Slide 25
Any questions?