## Slide 1
PowerPoint presentation
PowerPoint 11: Inspection and testing
Unit 114: Electrotechnical systems and equipment

## Slide 2: Inspection and testing
Inspection and testing is the procedure that electricians use to ensure that a circuit is working correctly and safe for use before being energised. It is a set of processes and procedures which must be followed and involves the use of test equipment to measure that the installation is functioning as expected in accordance with the wiring regulations.
It is an important part of every electrical job. An inspection and test is carried out to verify, so far as is reasonably practicable, that the requirements of BS 7671 (Wiring Regulations) and other relevant regulations have been met, during the job itself and after completion before handing over to the client. Inspection and testing should also be carried out for all electrical installations at regular intervals. It is applicable to domestic, commercial and industrial electrical work.

## Slide 3
It is important to protect the safety of people, livestock and property against the dangers and damage that electrical installations can cause. In basic terms this means assessing risk of injury from such hazards as:
electric shock
burns/fire
other moving equipment
power supply interruptions
arcing or burning.
Safety

## Slide 4
Before any testing is done, it is important that the installation is inspected. Examples of items to inspect are:
correct installation of cables
correct and firm fixing of equipment
terminations to ensure that they are correct and not loose
that the installation is in compliance with BS 7671
that the installation is in compliance with the project specification
that the installation is safe to use.
Inspection

## Slide 5: Test de-energised circuits: continuity of protective and bonding conductors
Why perform this test?
To verify that all circuits have a continuous connection to earth at all points of the circuit, and that all bonding conductors are continuous and of the correct CSA.
The instrument used is a low-resistance ohmmeter supplied from a source of between 4V and 24V.
The meter should have a resolution of at least 0.01Ω

## Slide 6
Water
pipe
Low-resistance ohnmeter
This test confirms continuity of the cpc.
Test de-energised circuits: continuity of protective and bonding conductors
Notes: Personal Notes

## Slide 7
Water
pipe
Low-resistance ohmmeter
The test leads are placed on either end of the conductor. This can be done by using a long test lead, as long as the resistance of the leads is deducted from the measurement taken.
The reading will be very low, it will relate to the length and size of the conductor being measured.
This is also the case for all supplementary bonding conductors, and the method used is the same.
Test de-energised circuits: continuity of protective and bonding conductors
Notes: Personal Notes

## Slide 8: Test de-energised circuits: insulation resistance
Why perform this test?
To ensure that there are no connections between live conductors and earth.

## Slide 9
Method:
Use the Megohm scale, choosing the correct voltage for the circuit being tested.
Ensure all switches are closed, and all lamps/loads and any electronic equipment are disconnected from the circuits.
Insulation resistance tester
Test de-energised circuits: insulation resistance

## Slide 10: Polarity test
The purpose of a polarity test is to ensure that all single pole devices (such as fuses, switches and circuit breakers) are connected in the line conductor only. Since ac installations consist of a live and a neutral conductor, it is extremely important that these conductors are connected the right way around, within all electrical accessories such as wall sockets or plugs.

## Slide 11
Polarity – Method 1
Low-resistance ohmmeter
Using the low ohms scale on the instrument, with the plate switch in the off position and the mcb closed, then the reading should be infinite, then… with the switch closed, there should be a low resistance value.
Polarity test
This verifies that the switch and the mcb is connected to the phase conductor only
Notes: Personal notes

## Slide 12
Place a temporary link between phase and earth in the dist board.
Low-resistance ohmmeter
Using the continuity/ ohm scale on the instrument, and with the plate switch in the off position and the mcb closed, then the reading should be infinite, then… with the switch closed, there should be a low resistance value.
This verifies that the switch and the mcb is connected to the line conductor only.
Polarity test – Method 2 (most common method used)
Notes: Personal notes

## Slide 13
Certification
On completion of the tests, the results should be recorded on the correct documentation, similar to the one shown.

## Slide 14
Any questions?