## Slide 1
PowerPoint presentation
PowerPoint 8: Cables and containment systems
Unit 114: Electrotechnical systems and equipment

## Slide 2: Suggested wiring system
Cable duct for power distribution cables
Steel infrastructure for installing steel wire armoured cables
Service risers for running power distribution cables – remember the fire barriers!

## Slide 3: Environmental conditions
      Before selecting a wiring system, you must also consider the environmental conditions that the installation will be subject to.
Ambient temperature
Select your cable to serve the highest operating temperature likely to be present.
Select enclosures which are suitable to withstand the highest working temperature – steel conduit and cable trunking, for example.

## Slide 4: Environmental conditions
Where water and dampness are present
If your installation is within a wet environment, then it must be designed to withstand such conditions. If damp, then ensure that all your termination points are suitable for the environment. Best to use PVC trunking and conduit systems.
Pollution and corrosion problems
If your installation is in a heavily dusty environment, then your enclosures must offer a degree of protection to international protection standards.

## Slide 5: Environmental conditions
Solar radiation
Ultraviolet light (UV) can discolour the sheath of PVC insulated cables and eventually crack and destroy the insulation. Any other PVC products used within the electrical industry can suffer the same outcome. Ensure that your chosen cable is compatible to the installation and that UV light will not cause problems in the future.
Current demand
BS 7671 tells us that all equipment installed must be suitable for the maximum power requirements by the current using equipment. This will mean paying particular attention to the cross-sectional area of your conductors.

## Slide 6: Advantages and limitations of common wiring systems and cable carriers
You must select the correct wiring system for each job. For example, you should not use PVC sheathed cable clipped directly to a surface to serve an industrial installation or bury this type of cable underground as a way of providing temporary power to a construction site.

## Slide 7: PVC sheathed flat profiled cable
Advantages
Inexpensive compared to other systems.
Quick to install.
Disadvantages
Open to accidental damage by other trades.
Must have all points of connection accessible when the installation is complete.

## Slide 8: Mineral insulated metal sheathed
Advantages
A good all-round cable which will resist impact damage.
Can be installed in hot and cold environments.
Disadvantages
Expensive and time consuming to install.
A high degree of skill and planning required to carry out installation.
Special tools are required to carry out the cable termination.

## Slide 9: PVC/SWA cable
Advantages
Robust and versatile.
Ideal for power requirements in industrial and commercial work and temporary installations serving construction sites.
Easy to terminate smaller sizes.
No special tools are required.

## Slide 10: PVC/SWA cable
Disadvantages
Can be heavy to install, sometimes requiring two operatives or more. The steel wire armouring is not strong enough to withstand accidents involving heavy construction plant.
When buried in the ground it requires the additional protection of sand, together with a yellow warning tape placed above the cable, or alternatively cable tiles may be placed above the installed cable.
When wiring for temporary installations the steel wire armouring will need to be checked if it is suitable for the earthing conductor.

## Slide 11: PVC insulated single core cable
Advantages
Ideal for cable trunking, conduit and panel wiring installations.
Easy to install.
Colours and sizes available to suit the needs of your installation.
Your installation can be added to, rewired and mixed sizes of cable can be used in trunking or conduit.

## Slide 12: PVC insulated single core cable
Disadvantages
Errors can occur with cable identification. Conductors can become trapped or friction- burnt when installing.
Too many conductors installed within the containment can sometimes cause warming to occur when the circuits are on load.

## Slide 13: Fire-retardant cable
Advantages
An ideal cable to use for fire alarm and central battery emergency lighting circuits. It can also be used for other sensitive circuits which require protection from potential fire.
It is light and easy to install and its red sheath colour identifies it from other cables

## Slide 14: Fire-retardant cable
Disadvantages
The insulation serving the cable cores is made from silicone rubber which, under conditions of extreme heat, chemically converts into silicon dioxide.
The cable can be expensive.
You must be very careful when removing the outer sheath not to snag the insulation around the conductor.

## Slide 15: Data cables
Data cables are used to transmit electronic information from a source to a destination. Extensively used in computer and telecommunication systems, the type of data cabling is either copper or fibre optics.

## Slide 16: Cable trunking
Cable trunking is an enclosure usually with a rectangular cross section, and with one removable or hinged side, that is used to protect cables and provide space for other electrical equipment.

## Slide 17: Cable trunking
Disadvantages
Easily get covered and/or filled with dust and dirt
Skilled worker needed
High cost
Advantages
It can hold a lot of wires/cables
More wires/cables can be added in the future
Good mechanical protection

## Slide 18: Cable tray
A cable tray system supports and protects both power and signal cables.
Most of the cable tray systems are open, allowing efficient heat dissipation and easy access for replacement and repairs. Although typically suspended from ceilings or affixed to walls, some cable tray systems are suitable for underfloor use.

## Slide 19: Types of cable trays
The following are popular cable tray types.
Ladder-type
Perforated type
Solid bottom type
Basket
Channel type

## Slide 20: Cable trays
Disadvantages:
The solid bottom cable tray system has a disadvantage in that moisture can build up in the cable trays.
Regular housekeeping is important for safety, as cable trays are often installed in hard to reach places.
Advantages:
Less expensive than other methods of protecting wiring on the production floor.
Maintenance: Cable trays are instantly visible for maintenance checks, changing of cables is easy because cables can enter or exit the tray at any point of the system.

## Slide 21: Conduit
A conduit wiring is a containment where the cable is enclosed in metal or plastic tubes. The conductor has insulation which is rated at the voltage required but gives no mechanical protection. By using a conduit system, the circuit can be rewired or altered as required and additional points added reasonably easily.

## Slide 22: Conduit
Advantages
It has a long life.
PVC conduits are highly resistant against corrosion.
Good mechanical protection.
Can be re-wired.
Disadvantages
Can be difficult to install.
Very hard to find a defect in the wiring.
The cost is high.

## Slide 23
Any questions?